## Heating Sizing
Simple Heating System Size: Washington State
This heating system sizing calculator is based on the Prescriptive Requirements of the 2018 Washington State Energy Code (WSEC) and ACCA Manuals J and S. This tool will calculate heating loads only. ACCA procedures for sizing cooling systems should be used to determine cooling loads. Please complete the green drop-downs and boxes that are applicable to your project. As you make selections in the drop-downs for each section, some values will be calculated for you. If you do not see the selection you need in the drop-down options, please contact the WSU Energy Program at energycode@energy.wsu.edu or (360) 956-2042 for assistance.
| Project Information | [7 empty] | Contact Information
Heating System Type:
To see detailed instructions for each section, place your cursor on the word "Instructions"
|  | Design Temperature | [6 empty] | Deisgn Temperature |  |  |  |  | _______
|  |  |  | Instructions |  |  | Select closest city |  | Design Temperature Difference (∆T) |  |  |  |  | _______
∆T = Indoor (70 degrees) - Outdoor Design Temp
Area of Building
Conditioned Floor Area
|  |  |  | Instructions |  | Conditioned Floor Area (sq ft)
|  |  | Average Ceiling Height | [7 empty] | Conditioned Volume
|  |  |  | Instructions |  | Average Ceiling Height (ft) |  |  | 8.5 |  | ________
|  | Glazing and Doors | [6 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | Select U-Factor |  | No selection |  |  |  | --
|  | Skylights | [6 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  |  |  | 0.5 |  |  |  | 0
Insulation
|  |  | Attic | [5 empty] | U-Factor | X | Area | = | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Single Rafter or Joist Vaulted Ceilings | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Above Grade Walls (see Figure 1) | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Floors | [5 empty] | U-Factor | X | Area |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
|  |  | Below Grade Walls and Slabs (see Figure 1) | [5 empty] | Wall U-Factor | X | Area |  | UA
|  |  |  | Instructions | Wall & Slab |  | Select Wall & Slab Insulation | [5 empty] | --
[5 empty] | Depth |  | Select nearest slab depth |  | Slab F-Factor | X | Length |  | UA
--
|  |  | Slab on Grade (see Figure 1) | [5 empty] | F-Factor | X | Length |  | UA
|  |  |  | Instructions |  |  | Select R-Value |  | No selection |  |  |  | --
Location of Ducts
|  |  |  | Instructions |  |  | Select Location of Ducts |  |  |  | Duct Leakage Coefficient
[8 empty] | Sum of UA |  |  |  |  | _________
[8 empty] | Envelope Heat Load |  |  |  |  | _________ | Btu / Hour
Sum of UA x ∆T
[8 empty] | Air Leakage Heat Load |  |  |  |  | _________ | Btu / Hour
Volume x 0.6 x ∆T x 0.018
[8 empty] | Building Design Heat Load |  |  |  |  | _________ | Btu / Hour
Air leakage + envelope heat loss
[8 empty] | Building and Duct Heat Load |  |  |  |  | _________ | Btu / Hour
Ducts in unconditioned space: sum of building heat loss x 1.10
Ducts in conditioned space: sum of building heat loss x 1
[8 empty] | Maximum Heat Equipment Output |  |  |  |  | _________ | Btu / Hour
Building and duct heat loss x 1.40 for forced air furnace
Building and duct heat loss x 1.25 for heat pump
Above Grade
Below Grade
Figure 1.
All Other Systems
Heat Pump
Note on G12: Using the drop-down, select the city that is closest to your building site.
Note on G17: Using exterior measurements, enter the square footage of living space conditioned directly or indirectly.
Note on G20: Enter the average ceiling height from your building plans.
Note on G23: Calculate and enter the total area of the vertical fenestration products (windows and doors) in the structure. Example: Window #1 area 10 ft2 Window #2 area 15 ft2 Total area 25 ft2 The glazing and doors portion of this calculator assumes the installed glazing products have an area weighted average U-factor
Note on G25: Calculate and enter the total area of the skylights in the structure. Example: Skylight #1 area 10 ft2 Skylight #2 area 15 ft2 Total area 25 ft2 The skylight portion of this calculator assumes the installed skylight products have an area weighted average U-factor of 0.30.
Note on G29: Using the drop-down, select the R-value specified in your building plans for flat and/or scissor truss ceilings. Then calculate and enter the area of the ceiling under attic insulated with the selected R-value.
Note on G32: Using the drop-down, select the R-value specified in your building plans for vaulted ceilings. Then calculate and enter the area of the vaulted ceiling insulated with the selected R-value. If there are no vaulted ceilings, select "No Vaulted Ceilings in this project"
Note on G35: Using the drop-down, select the R-value specified in your building plans for the above grade walls. Then calculate and enter the net above grade wall area. Net above grade wall area is the total above grade wall area minus the area of windows and doors. See Figure 1 for help understanding above and below grade.
Note on G38: Using the drop-down, select the R-value specified in your building plans for floors above unconditioned spaces. Then calculate and enter the floor area with the selected R-value.
Note on G41: Below-Grade Wall and Slab Description Using the drop-down, select the insulation specified in your building plans for below grade walls and slabs. Next, using the drop down select the depth (2', 3.5' or 7') that is nearest to the average depth below-grade of your slab. Below-Grade Wall Area: Calculate and enter the net below grade wall area. Net below grade wall area is the total below grade wall area minus the area of windows and doors. Slab Perimeter Calculate and enter the linear feet of perimeter of the slab below grade. For example, if the basement floor is a 54' x 32' slab below grade, the linear perimeter would be 172ft . 54'+54'+32'+32' = 172'
Note on G46: Using the drop-down, select the R-value specified in your building plans for slab on grade. Then calculate and enter the linear feet of perimeter of the slab on grade. For example, if the living room is a 20' x 30' slab on grade, the linear perimeter would be 100 ft. 20'+20'+30'+30'=100'
Note on G50: Using the drop-down, indicate if the majority of ducts will be installed in conditioned or unconditioned spaces. - If the majority of ducts will be installed in living areas, or if the heating system will be ductless, select "Conditioned Space" - If the majority of ducts will be installed in unconditioned space (crawlspace or unconditioned basement), select "Unconditioned Space"

## LookUps (hidden)
Each of these sections contain on row 2 the result of the selections, and three columns: a lookup number for formulas, selections for drop down boxes, and the measurement to use in the formulas.
Below Grade Walls and Slabs
Indoor Design Temperature |  | Outdoor Design Temperature |  |  | Vertical Glazing and Doors |  |  | Attic |  |  | Single Rafter or Joist Vaulted Ceilings |  |  | Above Grade Walls |  |  | Floors |  |  |  | Selection |  | Slab on Grade |  |  | Location of Ducts |  | Heating System Type | 2 | Linked to selection in row
[20 empty] | Wall & Slab | Select Wall & Slab Insulation
70 | Column1 | City | Temp | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor | Column1 | R-Value | U-Factor |  | Depth | Select nearest slab depth | Column1 | R-Value | F-Factor | Offset | location of ducts | Heat loss correction
| 1 | Select closest city |  | 1 | Select U-Factor | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection | 1 | Select R-Value | No selection |  | Search String | Select Wall & Slab Insulation, Select nearest slab depth | 1 | Select R-Value | No selection | 1 | Select Location of Ducts |  | Forced Air Furnace | 1 | 1.4
| 2 | Aberdeen 20 NNE | 25 | 2 | U-0.30 | 0.3 | 2 | R-60 | 0.024 | 2 | R-38 Advanced | 0.026 | 2 | R-21 Intermediate | 0.056 | 2 | R-30 | 0.029 |  | U | #N/A | 2 | R-10 Perimeter | 0.54 | 2 | Conditioned Space | 1 | Heat Pump | 2 | 1.25
| 3 | Anacortes | 24 | 3 | U-0.29 | 0.29 | 3 | R-60 Advanced | 0.17 | 3 | R-49 Advanced | 0.02 | 3 | R-21 INT plus R-4 ci | 0.043 | 3 | R-38 | 0.025 |  | F | #N/A | 3 | R-10 Fully Insulated | 0.36 | 3 | Unconditioned Space | 1.1
| 4 | Anatone | -4 | 4 | U-0.28 | 0.28 | 4 | R-49 | 0.026 | 4 | R-60 Advanced | 0.017 | 4 | R-21 INT plus R-12 ci | 0.032 | 4 | R-48 | 0.02 |  |  |  | 4 | No Slab on Grade in this project. | --- | 4 | No Ducts | 1
| 5 | Appleton | 11 | 5 | U-0.27 | 0.27 | 5 | R-49 Advanced | 0.02 | 5 | No Vaulted Ceilings in this project. | --- | 5 | R-21 INT plus R-16 ci | 0.028 | 5 | No Floors above unconditioned spaces. | ---
| 6 | Auburn | 25 | 6 | U-0.26 | 0.26 | 6 | R-38 | 0.031 | [10 empty] | DropDown_BelowGradeWalls
| 7 | Battleground | 19 | 7 | U-0.25 | 0.25 | 7 | R-38 Advanced | 0.026 | [10 empty] | Select Wall & Slab Insulation
| 8 | Bellevue | 24 | 8 | U-0.24 | 0.24 | [13 empty] | R0 Uninsulated
| 9 | Bellingham 2N | 19 | 9 | U-0.23 | 0.023 | [13 empty] | R10 Foam Ext
| 10 | Benton City 2 NW | 11 | 10 | U-0.22 | 0.22 | [13 empty] | R11 Batt
| 11 | Bickleton | 4 | 11 | U-0.21 | 0.021 | [13 empty] | R12 Foam Ext
| 12 | Blaine | 17 | 12 | U-0.20 | 0.2 | [13 empty] | R10 Foam Ext w/TB, R10 Full Underslab
| 13 | Bothell 2 N | 17 | 13 | U-0.19 | 0.019 | [13 empty] | R20 Foam Ext w/TB, R10 Full Underslab
| 14 | Bremerton | 29 | 14 | U-0.18 | 0.18 | [13 empty] | R21 Batt w/TB
| 15 | Brier | 24
| 16 | Buckley 1 NE | 26 | [16 empty] | DropDown_SlabDepth
| 17 | Bumping Lake | -5 | [16 empty] | Select nearest slab depth
| 18 | Burlington | 19 | [16 empty] | 2' depth
| 19 | Camas | 21 | [16 empty] | 3.5' depth
| 20 | Castle Rock | 23 | [16 empty] | 7' depth
| 21 | Cedar Lake | 20
| 22 | Centralia | 21
| 23 | Central Park | 27
| 24 | Chehalis | 21
| 25 | Chelan | 10
| 26 | Cheney | 4
| 27 | Chesaw | -11
| 28 | Chewalah 2 S | -9
| 29 | Chief Joseph Dam | 6
| 30 | Clallam Bay 1 NNE | 28
| 31 | Clarkston | 10
| 32 | Clearbrook | 19
| 33 | Clearwater | 26
| 34 | Cle Elum | 1
| 35 | Clyde Hill | 24
| 36 | Colfax 1 NW | 2
| 37 | College Place | 6
| 38 | Colville AP | -2
| 39 | Conconully | -7
| 40 | Concrete | 19
| 41 | Connell 4 NNW | 6
| 42 | Cougar 5 E | 25
| 43 | Coulee Dam 1 SW | 9
| 44 | Coupeville 1 S | 21
| 45 | Cushman Dam | 22
| 46 | Dallesport AP | 14
| 47 | Darrington RS | 13
| 48 | Davenport | 5
| 49 | Dayton 1 WSW | 5
| 50 | Deer Park 2 E | -5
| 51 | Des Moines | 25
| 52 | Diablo Dam | 15
| 53 | Dishman | 9
| 54 | East Bremerton | 29
| 55 | Edmonds | 24
| 56 | Electron Headwks | 16
| 57 | Ellensburg AP | 2
| 58 | Elma | 24
| 59 | Eltopia 6 W | 9
| 60 | Elwha RS | 24
| 61 | Enumclaw | 26
| 62 | Ephrata AP | 7
| 63 | Everett JC | 23
| 64 | Everett Paine AFB | 21
| 65 | Fircrest | 29
| 66 | Forks I E | 23
| 67 | Fort Lewis | 24
| 68 | Fruitvale | 1.1
| 69 | Glacier RS | 13
| 70 | Glenoma (Kosmos) | 18
| 71 | Goldendale | 7
| 72 | Grandview | 12
| 73 | Grapeview | 30
| 74 | Grayland 2 S | 28
| 75 | Grays River Hatchery | 24
| 76 | Greenwater | 1.4
| 77 | Grotto | 21
| 78 | Harrington 2 S | 3
| 79 | Hartline | 7
| 80 | Hatton 8 E | 1
| 81 | Holden Village | 4
| 82 | Hoquiam AP | 26
| 83 | Ice Harbor Dam | 17
| 84 | Inchelium 2 NW | 0
| 85 | Issaquah | 23
| 86 | John Day Dam | 19
| 87 | Kelso AP | 24
| 88 | Kennewick 10 SW | 13
| 89 | Kent | 21
| 90 | Kid Valley | 20
| 91 | Kirkland | 17
| 92 | Lacey | 17
| 93 | Lacrosse 3 ESE | -3
| 94 | La Grande | 23
| 95 | Lake Cle Elum | -4
| 96 | Lake Forest Park | 20
| 97 | Lake Kachess | -2
| 98 | Lake Keechelus | 0
| 99 | Lakewood Center | 23
| 100 | Landsburg | 18
| 101 | Larson AFB | 6
| 102 | Laurier | -8
| 103 | Leavenworth | -3
| 104 | Lemanasky Lake | -7
| 105 | Lind 3 NE | 6
| 106 | Linwood | 10
| 107 | Little Goose Dam | 22
| 108 | Long Beach 3 NNE | 25
| 109 | Longview | 24
| 110 | Lower Granite Dam | 14
| 111 | Lower Monument Dam | 18
| 112 | Lynden | 18
| 113 | Lynnwood | 24
| 114 | Maloft | 4
| 115 | Marietta 3 NNW | 18
| 116 | Marysville | 23
| 117 | McMillin Res. | 21
| 118 | McNary Dam | 11
| 119 | Medical Lake | 4
| 120 | Medina | 24
| 121 | Mercer Island | 25
| 122 | Metaline Falls | -1
| 123 | Methow 2 W | 1
| 124 | Mountlake Terrace | 22
| 125 | Mt. Spokane Summit | -2
| 126 | Mount Vernon 3 WNW | 20
| 127 | Moxee City 10 E | 8
| 128 | Mud Mtn. Dam | 23
| 129 | Nespelem 2 S | -4
| 130 | Newhalem | 19
| 131 | Newport | -5
| 132 | Normandy Park | 24
| 133 | Northport | 2
| 134 | Oak Harbor | 16
| 135 | Oakville | 20
| 136 | Odessa | 7
| 137 | Olga 2 SE | 24
| 138 | Olympia, AP. | 17
| 139 | Omak 2 NW | 3
| 140 | Opportunity | 8
| 141 | Oroville | 5
| 142 | Othello | 9
| 143 | Packwood | 16
| 144 | Palmer 3 SE | 22
| 145 | Parkland | 20
| 146 | Pasco | 13
| 147 | Plain | -3
| 148 | Pleasant View | 16
| 149 | Pt. Grenville | 27
| 150 | Pomeroy | 3
| 151 | Port Angeles | 28
| 152 | Port Orchard | 29
| 153 | Port Townsend | 25
| 154 | Priest Rapids Dam | 14
| 155 | Prosser | 12
| 156 | Pullman Exp. Sta. | 1
| 157 | Puyallup | 19
| 158 | Quilcene 2 SW | 23
| 159 | Quillayute AP | 23
| 160 | Quinault RS | 25
| 161 | Quincy 1 NE | 4
| 162 | Rainier, Longmire | 15
| 163 | Paradise RS | 8
| 164 | Raymond | 28
| 165 | Redmond | 17
| 166 | Renton | 24
| 167 | Republic | -9
| 168 | Richland | 11
| 169 | Rimrock Tieton Dam | 4
| 170 | Ritzville | 6
| 171 | Rosalia | 6
| 172 | Ross Dam | 14
| 173 | St. John | 15
| 174 | Sappho 8 E | 23
| 175 | Satus Pass | 10
| 176 | Seattle: Sea-Tac AP | 24
| 177 | Sedro Woolley 1 E | 19
| 178 | Selah | 11
| 179 | Sequim | 23
| 180 | Shelton | 23
| 181 | Shoultes | 23
| 182 | Skamania Fish Hatch. | 24
| 183 | Smyrna | 8
| 184 | Snohomish | 21
| 185 | Snoqualmie Falls | 22
| 186 | Snoqualmie Pass | 6
| 187 | South Broadway | 11
| 188 | So. Olympic Tree Farm | 24
| 189 | Spanaway | 20
| 190 | Spokane AP | 4
| 191 | Spokane CO | 10
| 192 | Spokane Fairchild AFB | 4
| 193 | Sprague | 4
| 194 | Stampede Pass | 7
| 195 | Startup 1 E | 20
| 196 | Stehekin 3 NW | 12
| 197 | Steilacoom | 21
| 198 | Stevens Pass | 6
| 199 | Stockdill Ranch | -14
| 200 | Sumner | 19
| 201 | Sunnyside | 12
| 202 | Tacoma McChord | 21
| 203 | Tacoma CO | 29
| 204 | Tatoosh Island | 31
| 205 | Thompson Place | 20
| 206 | Tietort Intake | 6
| 207 | Toledo AP | 17
| 208 | Toppenish | 11
| 209 | Trinidad 2 SSE | 13
| 210 | Tukwila | 24
| 211 | Tumwater | 17
| 212 | University Place | 29
| 213 | Upper Baker Dam | 14
| 214 | Vancouver | 22
| 215 | Vashon Island | 28
| 216 | Walla Walla AP | 6
| 217 | Walla Walla CO | 13
| 218 | Wapato | 10
| 219 | Washougal 8 ENE | 21
| 220 | Waterville | 1
| 221 | Wawawai 2 NW | 14
| 222 | Wellpinit | 1
| 223 | Wenatchee AP | 13
| 224 | Wenatchee CO | 10
| 225 | West Clarkston | 10
| 226 | Whidbey Island | 11
| 227 | White River RS | 12
| 228 | White Swan RS | 8
| 229 | Whitman Mission | 11
| 230 | Wilbur | 4
| 231 | Willapa Harbor | 26
| 232 | Wilson Creek | 3
| 233 | Wind River | 15
| 234 | Winthrop 1 WSW | -12
| 235 | Yakima AP | 11

## Weather Data (hidden)
Select closest city
Aberdeen 20 NNE | 25
Anacortes | 24
Anatone | -4
Appleton | 11
Auburn | 25
Battleground | 19
Bellevue | 24
Bellingham 2N | 19
Benton City 2 NW | 11
Bickleton | 4
Blaine | 17
Bothell 2 N | 17
Bremerton | 29
Brier | 24
Buckley 1 NE | 26
Bumping Lake | -5
Burlington | 19
Camas | 21
Castle Rock | 23
Cedar Lake | 20
Centralia | 21
Central Park | 27
Chehalis | 21
Chelan | 10
Cheney | 4
Chesaw | -11
Chewalah 2 S | -9
Chief Joseph Dam | 6
Clallam Bay 1 NNE | 28
Clarkston | 10
Clearbrook | 19
Clearwater | 26
Cle Elum | 1
Clyde Hill | 24
Colfax 1 NW | 2
College Place | 6
Colville AP | -2
Conconully | -7
Concrete | 19
Connell 4 NNW | 6
Cougar 5 E | 25
Coulee Dam 1 SW | 9
Coupeville 1 S | 21
Cushman Dam | 22
Dallesport AP | 14
Darrington RS | 13
Davenport | 5
Dayton 1 WSW | 5
Deer Park 2 E | -5
Des Moines | 25
Diablo Dam | 15
Dishman | 9
East Bremerton | 29
Edmonds | 24
Electron Headwks | 16
Ellensburg AP | 2
Elma | 24
Eltopia 6 W | 9
Elwha RS | 24
Enumclaw | 26
Ephrata AP | 7
Everett JC | 23
Everett Paine AFB | 21
Fircrest | 29
Forks I E | 23
Fort Lewis | 24
Fruitvale | 1.1
Glacier RS | 13
Glenoma (Kosmos) | 18
Goldendale | 7
Grandview | 12
Grapeview | 30
Grayland 2 S | 28
Grays River Hatchery | 24
Greenwater | 1.4
Grotto | 21
Harrington 2 S | 3
Hartline | 7
Hatton 8 E | 1
Holden Village | 4
Hoquiam AP | 26
Ice Harbor Dam | 17
Inchelium 2 NW | 0
Issaquah | 23
John Day Dam | 19
Kelso AP | 24
Kennewick 10 SW | 13
Kent | 21
Kid Valley | 20
Kirkland | 17
Lacey | 17
Lacrosse 3 ESE | -3
La Grande | 23
Lake Cle Elum | -4
Lake Forest Park | 20
Lake Kachess | -2
Lake Keechelus | 0
Lakewood Center | 23
Landsburg | 18
Larson AFB | 6
Laurier | -8
Leavenworth | -3
Lemanasky Lake | -7
Lind 3 NE | 6
Linwood | 10
Little Goose Dam | 22
Long Beach 3 NNE | 25
Longview | 24
Lower Granite Dam | 14
Lower Monument Dam | 18
Lynden | 18
Lynnwood | 24
Maloft | 4
Marietta 3 NNW | 18
Marysville | 23
McMillin Res. | 21
McNary Dam | 11
Medical Lake | 4
Medina | 24
Mercer Island | 25
Metaline Falls | -1
Methow 2 W | 1
Mountlake Terrace | 22
Mt. Spokane Summit | -2
Mount Vernon 3 WNW | 20
Moxee City 10 E | 8
Mud Mtn. Dam | 23
Nespelem 2 S | -4
Newhalem | 19
Newport | -5
Normandy Park | 24
Northport | 2
Oak Harbor | 16
Oakville | 20
Odessa | 7
Olga 2 SE | 24
Olympia, AP. | 17
Omak 2 NW | 3
Opportunity | 8
Oroville | 5
Othello | 9
Packwood | 16
Palmer 3 SE | 22
Parkland | 20
Pasco | 13
Plain | -3
Pleasant View | 16
Pt. Grenville | 27
Pomeroy | 3
Port Angeles | 28
Port Orchard | 29
Port Townsend | 25
Priest Rapids Dam | 14
Prosser | 12
Pullman Exp. Sta. | 1
Puyallup | 19
Quilcene 2 SW | 23
Quillayute AP | 23
Quinault RS | 25
Quincy 1 NE | 4
Rainier, Longmire | 15
Paradise RS | 8
Raymond | 28
Redmond | 17
Renton | 24
Republic | -9
Richland | 11
Rimrock Tieton Dam | 4
Ritzville | 6
Rosalia | 6
Ross Dam | 14
St. John | 15
Sappho 8 E | 23
Satus Pass | 10
Seattle: Sea-Tac AP | 24
Sedro Woolley 1 E | 19
Selah | 11
Sequim | 23
Shelton | 23
Shoultes | 23
Skamania Fish Hatch. | 24
Smyrna | 8
Snohomish | 21
Snoqualmie Falls | 22
Snoqualmie Pass | 6
South Broadway | 11
So. Olympic Tree Farm | 24
Spanaway | 20
Spokane AP | 4
Spokane CO | 10
Spokane Fairchild AFB | 4
Sprague | 4
Stampede Pass | 7
Startup 1 E | 20
Stehekin 3 NW | 12
Steilacoom | 21
Stevens Pass | 6
Stockdill Ranch | -14
Sumner | 19
Sunnyside | 12
Tacoma McChord | 21
Tacoma CO | 29
Tatoosh Island | 31
Thompson Place | 20
Tietort Intake | 6
Toledo AP | 17
Toppenish | 11
Trinidad 2 SSE | 13
Tukwila | 24
Tumwater | 17
University Place | 29
Upper Baker Dam | 14
Vancouver | 22
Vashon Island | 28
Walla Walla AP | 6
Walla Walla CO | 13
Wapato | 10
Washougal 8 ENE | 21
Waterville | 1
Wawawai 2 NW | 14
Wellpinit | 1
Wenatchee AP | 13
Wenatchee CO | 10
West Clarkston | 10
Whidbey Island | 11
White River RS | 12
White Swan RS | 8
Whitman Mission | 11
Wilbur | 4
Willapa Harbor | 26
Wilson Creek | 3
Wind River | 15
Winthrop 1 WSW | -12
Yakima AP | 11

## Below Grade Walls & Slabs (hidden)
WSU Code Compliance Calculator - WSEC 2015 &2018 | [5 empty] | (C) 2020
Below Grade Walls and Slabs - Updated to WSEC 2018, Appendix A, Table A104.1 (values changed from WSEC 2015 Appendix A)
Index |  | Component Description | Reference | Wall U | Slab F
1
2 |  | === Most Frequently Used =========
3 | 2' depth | R0 Uninsulated, 2' depth | 10-1 | 0.331 | 0.58
4 | 2' depth | R10 Foam Ext, 2' depth | 10-1 | 0.271 | 0.51
5 | 2' depth | R11 Batt, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.185 | 0.43 | Updated to WSEC 2018
6 | 2' depth | R12 Foam Ext, 2' depth | 10-1 | 0.058 | 0.47 | Updated to WSEC 2018
7 | 2' depth | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 10-1 | 0.055 | 0.293 | Updated to WSEC 2018
8 | 2' depth | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.307 | Updated to WSEC 2018
9 | 2' depth | R21 Batt w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.505 | Added 2020
10 | 3.5' depth | R0 Uninsulated, 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.271 | 0.51 | Updated to WSEC 2018
11 | 3.5' depth | R10 Foam Ext, 3.5' depth | 10-1 | 0.075 | 0.52 | Updated to WSEC 2018
12 | 3.5' depth | R11 Batt, 3.5' depth | WSU | 0.058 | 0.61 | Updated to WSEC 2018
13 | 3.5' depth | R12 Foam Ext, 3.5' depth | WSU | 0.057 | 0.57 | Updated to WSEC 2018
14 | 3.5' depth | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | WSU | 0.064 | 0.324 | Added 2020
15 | 3.5' depth | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | WSU | 0.038 | 0.331 | Added 2020 from reference
16 | 3.5' depth | R21 Batt w/TB, 3.5' depth | WSU | 0.04 | 0.56 | Updated to WSEC 2018
17 | 7' depth | R0 Uninsulated, 7' depth | 10-1 | 0.185 | 0.43 | Updated to WSEC 2018
18 | 7' depth | R10 Foam Ext, 7' depth | 10-1 | 0.058 | 0.47 | Updated to WSEC 2018
19 | 7' depth | R11 Batt, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.051 | 0.541 | Updated to WSEC 2018
20 | 7' depth | R12 Foam Ext, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.05 | 0.42 | Updated to WSEC 2018
21 | 7' depth | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.055 | 0.293 | Added 2020
22 | 7' depth | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | WSU | 0.034 | 0.304 | Added 2020 from reference
23 | 7' depth | R21 Batt w/TB, 7' depth | WSU | 0.035 | 0.5 | Updated to WSEC 2018
24 | 10 | ============================
25 | 2' depth | R0 Uninsulated, 2' depth | 10-1 | 0.331 | 0.58 | Updated to WSEC 2018
26 | 2' depth | R10 Foam Ext, 2' depth | 10-1 | 0.089 | 0.56 | Updated to WSEC 2018
27 | 2' depth | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.068 | 0.345 | Added 2020
28 | 2' depth | R11 Batt, 2' depth | 10-1 | 0.063 | 0.67 | Updated to WSEC 2018
29 | 2' depth | R11 Batt w/TB, 2' depth | 10-1 | 0.065 | 0.59 | Updated to WSEC 2018
30 | 2' depth | R11 Batt + R5 ci, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.044 | 0.677 | Added 2023 from reference
31 | 2' depth | R11 Batt + R5 ci w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.046 | 0.59 | Added 2020 from reference
32 | 2' depth | R11 Batt + R5 ci R10 Fully Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.048 | 0.348 | Added 2020 from reference
33 | 2' depth | R12 Foam Ext, 2' depth | 10-1 | 0.61 | 0.6 | Updated to WSEC 2018
34 | 2' depth | R13 Batt, 2' depth | WSU | 0.056007 | 0.67333 | Interpolated between R11 and R19
35 | 2' depth | R13 Batt w/TB , 2' depth | WSU | 0.05834 | 0.59 | Interpolated between R11 and R19
36 | 2' depth | R13 Batt + R5 ci, 2' depth | WSU | 0.040337 | 0.67867 | Interpolated between R11 and R19
37 | 2' depth | R15 Batt, 2' depth | WSU | 0.0525 | 0.675 | Interpolated between R11 and R19
38 | 2' depth | R15 Batt w/TB, 2' depth | WSU | 0.055 | 0.59 | Interpolated between R11 and R19
39 | 2' depth | R19 Batt, 2' depth | 10-1 | 0.042 | 0.68 | Updated to WSEC 2018
40 | 2' depth | R19 Batt w/TB, 2' depth | 10-1 | 0.045 | 0.59 | Updated to WSEC 2018
41 | 2' depth | R19 Batt + R5 ci, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.033 | 0.682 | Added 2023 from reference
42 | 2' depth | R19 Batt + R5 ci w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.594 | Added 2023 from reference
43 | 2' depth | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.35 | Added 2020 from reference
44 | 2' depth | R21 Batt, 2' depth | WSU | 0.04 | 0.68 | Updated to WSEC 2018
45 | 2' depth | R21 Batt w/TB, 2' depth | WSU | 0.042 | 0.59 | Updated to WSEC 2018
46 | 2' depth | R21 Batt + R5 ci, 2' depth | 10-1 | 0.031 | 0.68 | Added in WSEC 2018
47 | 2' depth | R21 Batt + R5 ci w/TB, 2' depth | 10-1 | 0.032 | 0.59 | Added in WSEC 2018
48 | 2' depth | R21 Batt + R7 ci, 2' depth | 10-1 | 0.029 | 0.68 | Added in WSEC 2018
49 | 2' depth | R21 Batt + R7 ci w/TB, 2' depth | 10-1 | 0.03 | 0.59 | Added in WSEC 2018
50 | 2' depth | R21 Batt + R5 ci R10 Fully Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.031 | 0.35 | Added 2020 from reference
51 | 2' depth | R25 Batt w/TB, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.593 | Added 2020 from reference
52 | 2' depth | R25 Batt w/TB, R10 Full Underslab, 2' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.35 | Added 2020 from reference
53 | 3.5' depth | R0 Uninsulated, 3.5' depth | 10-1 | 0.271 | 0.51 | Updated to WSEC 2018
54 | 3.5' depth | R11 Batt 3.5' depth | 10-1 | 0.075 | 0.52 | Updated to WSEC 2018
55 | 3.5' depth | R11 Batt 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.064 | 0.324 | Added 2020
56 | 3.5' depth | R11 Batt + R5 ci 3.5' depth | 10-1 | 0.058 | 0.61 | Updated to WSEC 2018
57 | 3.5' depth | R11 Batt + R5 ci 3.5' depth w/TB | 10-1 | 0.061 | 0.55 | Updated to WSEC 2018
58 | 3.5' depth | R11 Batt + R5 ci 3.5' depth R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.042 | 0.624 | Added 2023 from reference
59 | 3.5' depth | R13 Batt 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.043 | 0.553 | Added 2020 from reference
60 | 3.5' depth | R13 Batt + R5 ci 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.045 | 0.329 | Added 2020 from reference
61 | 3.5' depth | R13 Batt 3.5' depth w/TB | 10-1 | 0.057 | 0.57 | Updated to WSEC 2018 | [7 empty] | Figures from: Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf
62 | 3.5' depth | R15 Batt 3.5' depth | WSU | 0.052339 | 0.61333 | Interpolated between R11 and R19
63 | 3.5' depth | R15 Batt 3.5' depth w/TB | WSU | 0.054673 | 0.55 | Interpolated between R11 and R19
64 | 3.5' depth | R19 Batt 3.5' depth | WSU | 0.038337 | 0.626 | Interpolated between R11 and R19
65 | 3.5' depth | R19 Batt 3.5' depth w/TB | WSU | 0.0495 | 0.615 | Interpolated between R11 and R19
66 | 3.5' depth | R19 Batt + R5 ci 3.5' depth | WSU | 0.0515 | 0.55 | Interpolated between R11 and R19
67 | 3.5' depth | R19 Batt + R5 ci 3.5' depth w/TB | 10-1 | 0.041 | 0.62 | Updated to WSEC 2018
68 | 3.5' depth | R21 Batt 3.5' depth | 10-1 | 0.042 | 0.55 | Updated to WSEC 2018
69 | 3.5' depth | R21 Batt 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.031 | 0.63 | Added 2023 from reference
70 | 3.5' depth | R21 Batt + R5 ci 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.033 | 0.558 | Added 2023 from reference
71 | 3.5' depth | R21 Batt + R5 ci 3.5' depth w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.331 | Added 2020 from reference
72 | 3.5' depth | R21 Batt + R7 ci 3.5' depth | WSU | 0.038 | 0.63 | Updated to WSEC 2018
73 | 3.5' depth | R21 Batt + R7 ci 3.5' depth w/TB | WSU | 0.04 | 0.56 | Updated to WSEC 2018
74 | 3.5' depth | R21 Batt + R5 ci 3.5' depth R10 Fully Underslab | 10-1 | 0.03 | 0.632 | Added in WSEC 2018
75 | 3.5' depth | R25 Batt 3.5' depth w/TB | 10-1 | 0.031 | 0.56 | Added in WSEC 2018
76 | 3.5' depth | R25 Batt 3.5' depth w/TB, R10 Full Underslab | 10-1 | 0.027 | 0.63 | Added in WSEC 2018
77 | 3.5' depth | R-20 perimeter, 3.5' depth w/TB, R10 Full Underslab | 10-1 | 0.029 | 0.56 | Added in WSEC 2018
78 | 3.5' depth | R10 Foam Ext 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.333 | Added 2020 from reference
79 | 3.5' depth | R12 Foam Ext 3.5' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.036 | 0.557 | Added 2020 from reference
80 | 3.5' depth | R10 Perimeter 3.5' depth w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.331 | Added 2020 from reference
81 | 7' depth | R0 Uninsulated, 7' depth | 10-1 | 0.185 | 0.43 | Updated to WSEC 2018
82 | 7' depth | R10 Foam Ext, 7' depth | 10-1 | 0.058 | 0.47 | Updated to WSEC 2018
83 | 7' depth | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.055 | 0.293 | Added 2020
84 | 7' depth | R11 Batt, 7' depth | 10-1 | 0.051 | 0.541 | Updated to WSEC 2018
85 | 7' depth | R11 Batt w/TB, 7' depth | 10-1 | 0.053 | 0.49 | Updated to WSEC 2018
86 | 7' depth | R11 Batt + R5 ci, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.037 | 0.553 | Added 2023 from reference
87 | 7' depth | R11 Batt + R5 ci w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.038 | 0.499 | Added 2020 from reference
88 | 7' depth | R11 Batt + R5 ci R10 Fully Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.04 | 0.301 | Added 2020 from reference
89 | 7' depth | R12 Foam Ext, 7' depth | 10-1 | 0.05 | 0.42 | Updated to WSEC 2018
90 | 7' depth | R13 Batt, 7' depth | WSU | 0.046005 | 0.54067 | Interpolated between R11 and R19
91 | 7' depth | R13 Batt w/TB , 7' depth | WSU | 0.047672 | 0.49333 | Interpolated between R11 and R19
92 | 7' depth | R13 Batt + R5 ci, 7' depth | WSU | 0.034003 | 0.55633 | Interpolated between R11 and R19
93 | 7' depth | R15 Batt, 7' depth | WSU | 0.0435 | 0.5405 | Interpolated between R11 and R19
94 | 7' depth | R15 Batt w/TB, 7' depth | WSU | 0.045 | 0.495 | Interpolated between R11 and R19
95 | 7' depth | R19 Batt, 7' depth | 10-1 | 0.036 | 0.54 | Updated to WSEC 2018
96 | 7' depth | R19 Batt w/TB, 7' depth | 10-1 | 0.037 | 0.5 | Updated to WSEC 2018
97 | 7' depth | R19 Batt + R5 ci, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.028 | 0.563 | Added 2023 from reference
98 | 7' depth | R19 Batt + R5 ci w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.507 | Added 2023 from reference
99 | 7' depth | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.304 | Added 2020 from reference
100 | 7' depth | R21 Batt, 7' depth | WSU | 0.035 | 0.56 | Updated to WSEC 2018
101 | 7' depth | R21 Batt w/TB, 7' depth | WSU | 0.035 | 0.5 | Updated to WSEC 2018
102 | 7' depth | R21 Batt + R5 ci, 7' depth | 10-1 | 0.027 | 0.56 | Added in WSEC 2018
103 | 7' depth | R21 Batt + R5 ci w/TB, 7' depth | 10-1 | 0.028 | 0.51 | Added in WSEC 2018
104 | 7' depth | R21 Batt + R7 ci, 7' depth | 10-1 | 0.025 | 0.57 | Added in WSEC 2018
105 | 7' depth | R21 Batt + R7 ci w/TB, 7' depth | 10-1 | 0.026 | 0.57 | Added in WSEC 2018
106 | 7' depth | R21 Batt + R5 ci R10 Fully Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.029 | 0.307 | Added 2020 from reference
107 | 7' depth | R25 Batt w/TB, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.032 | 0.505 | Added 2020 from reference
108 | 7' depth | R25 Batt w/TB, R10 Full Underslab, 7' depth | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | 0.034 | 0.304 | Added 2020 from reference
109 | Depth | == Custom Entries per WSEC R402.1.5 U-factor Reference and Calculations ======== |  | Wall U | Slab F | Notes
110 |  | Test slab | Custom | 0.05 | 0.5
111 |  |  | Custom
112 |  |  | Custom
113 |  |  | Custom
114 |  |  | Custom
115 |  |  | Custom
116 |  |  | Custom
117 |  |  | Custom
If you rearrange, add or delete rows below -- be sure to make corresponding changes to the six areas above.
|  | DropDown_BelowGradeSlab |  |  | Component Description | Wall U | Slab F | Component Description | Wall U | Slab F | Component Description | Wall U | Slab F
1 |  |  | Reference | Notes | 2' depth |  |  | 3.5' depth |  |  | 7' depth
2 |  | === Most Frequently Used =========
3 |  | R0 Uninsulated | 10-1 | Updated to WSEC 2018 | R0 Uninsulated, 2' depth | 0.331 | 0.58 | R0 Uninsulated, 3.5' depth | 0.271 | 0.51 | R0 Uninsulated, 7' depth | 0.185 | 0.43
4 |  | R10 Foam Ext | 10-1 | Updated to WSEC 2018 | R10 Foam Ext, 2' depth | 0.089 | 0.56 | R10 Foam Ext, 3.5' depth | 0.075 | 0.52 | R10 Foam Ext, 7' depth | 0.058 | 0.47
5 |  | R11 Batt | 10-1 | Updated to WSEC 2018 | R11 Batt, 2' depth | 0.063 | 0.67 | R11 Batt, 3.5' depth | 0.058 | 0.61 | R11 Batt, 7' depth | 0.051 | 0.541
6 |  | R12 Foam Ext | 10-1 | Updated to WSEC 2018 | R12 Foam Ext, 2' depth | 0.61 | 0.6 | R12 Foam Ext, 3.5' depth | 0.057 | 0.57 | R12 Foam Ext, 7' depth | 0.05 | 0.42
7 |  | R10 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.068 | 0.345 | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.064 | 0.324 | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.055 | 0.293
8 |  | R20 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
9 |  | R21 Batt w/TB | WSU | Updated to WSEC 2018 | R21 Batt w/TB, 2' depth | 0.042 | 0.59 | R21 Batt w/TB, 3.5' depth | 0.04 | 0.56 | R21 Batt w/TB, 7' depth | 0.035 | 0.5
10 |  | ============================
11 |  | R0 Uninsulated | 10-1 | Updated to WSEC 2018 | R0 Uninsulated, 2' depth | 0.331 | 0.58 | R0 Uninsulated, 3.5' depth | 0.271 | 0.51 | R0 Uninsulated, 7' depth | 0.185 | 0.43
12 |  | R10 Foam Ext | 10-1 | Updated to WSEC 2018 | R10 Foam Ext, 2' depth | 0.089 | 0.56 | R10 Foam Ext, 3.5' depth | 0.075 | 0.52 | R10 Foam Ext, 7' depth | 0.058 | 0.47
13 |  | R10 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 | R10 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.068 | 0.345 | R10 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.064 | 0.324 | R10 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.055 | 0.293
14 |  | R11 Batt | 10-1 | Updated to WSEC 2018 | R11 Batt, 2' depth | 0.063 | 0.67 | R11 Batt, 3.5' depth | 0.058 | 0.61 | R11 Batt, 7' depth | 0.051 | 0.541
15 |  | R11 Batt w/TB | 10-1 | Updated to WSEC 2018 | R11 Batt w/TB, 2' depth | 0.065 | 0.59 | R11 Batt w/TB, 3.5' depth | 0.061 | 0.55 | R11 Batt w/TB, 7' depth | 0.053 | 0.49
16 |  | R11 Batt + R5 ci | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R11 Batt + R5 ci, 2' depth | 0.044 | 0.677 | R11 Batt + R5 ci, 3.5' depth | 0.042 | 0.624 | R11 Batt + R5 ci, 7' depth | 0.037 | 0.553
17 |  | R11 Batt + R5 ci w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R11 Batt + R5 ci w/TB, 2' depth | 0.046 | 0.59 | R11 Batt + R5 ci w/TB, 3.5' depth | 0.043 | 0.553 | R11 Batt + R5 ci w/TB, 7' depth | 0.038 | 0.499
18 |  | R11 Batt + R5 ci R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R11 Batt + R5 ci R10 Fully Underslab, 2' depth | 0.048 | 0.348 | R11 Batt + R5 ci R10 Fully Underslab, 3.5' depth | 0.045 | 0.329 | R11 Batt + R5 ci R10 Fully Underslab, 7' depth | 0.04 | 0.301
19 |  | R12 Foam Ext | 10-1 | Updated to WSEC 2018 | R12 Foam Ext, 2' depth | 0.61 | 0.6 | R12 Foam Ext, 3.5' depth | 0.057 | 0.57 | R12 Foam Ext, 7' depth | 0.05 | 0.42
20 |  | R13 Batt | WSU | Interpolated between R11 and R19 | R13 Batt, 2' depth | 0.056007 | 0.67333 | R13 Batt, 3.5' depth | 0.052339 | 0.61333 | R13 Batt, 7' depth | 0.046005 | 0.54067
21 |  | R13 Batt w/TB | WSU | Interpolated between R11 and R19 | R13 Batt w/TB , 2' depth | 0.05834 | 0.59 | R13 Batt w/TB , 3.5' depth | 0.054673 | 0.55 | R13 Batt w/TB , 7' depth | 0.047672 | 0.49333
22 |  | R13 Batt + R5 ci | WSU | Interpolated between R11 and R19 | R13 Batt + R5 ci, 2' depth | 0.040337 | 0.67867 | R13 Batt + R5 ci, 3.5' depth | 0.038337 | 0.626 | R13 Batt + R5 ci, 7' depth | 0.034003 | 0.55633
23 |  | R15 Batt | WSU | Interpolated between R11 and R19 | R15 Batt, 2' depth | 0.0525 | 0.675 | R15 Batt, 3.5' depth | 0.0495 | 0.615 | R15 Batt, 7' depth | 0.0435 | 0.5405
24 |  | R15 Batt w/TB | WSU | Interpolated between R11 and R19 | R15 Batt w/TB, 2' depth | 0.055 | 0.59 | R15 Batt w/TB, 3.5' depth | 0.0515 | 0.55 | R15 Batt w/TB, 7' depth | 0.045 | 0.495
25 |  | R19 Batt | 10-1 | Updated to WSEC 2018 | R19 Batt, 2' depth | 0.042 | 0.68 | R19 Batt, 3.5' depth | 0.041 | 0.62 | R19 Batt, 7' depth | 0.036 | 0.54
26 |  | R19 Batt w/TB | 10-1 | Updated to WSEC 2018 | R19 Batt w/TB, 2' depth | 0.045 | 0.59 | R19 Batt w/TB, 3.5' depth | 0.042 | 0.55 | R19 Batt w/TB, 7' depth | 0.037 | 0.5
27 |  | R19 Batt + R5 ci | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R19 Batt + R5 ci, 2' depth | 0.033 | 0.682 | R19 Batt + R5 ci, 3.5' depth | 0.031 | 0.63 | R19 Batt + R5 ci, 7' depth | 0.028 | 0.563
28 |  | R19 Batt + R5 ci w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2023 from reference | R19 Batt + R5 ci w/TB, 2' depth | 0.034 | 0.594 | R19 Batt + R5 ci w/TB, 3.5' depth | 0.033 | 0.558 | R19 Batt + R5 ci w/TB, 7' depth | 0.029 | 0.507
29 |  | R20 Foam Ext w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R20 Foam Ext w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R20 Foam Ext w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R20 Foam Ext w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
30 |  | R21 Batt | WSU | Updated to WSEC 2018 | R21 Batt, 2' depth | 0.04 | 0.68 | R21 Batt, 3.5' depth | 0.038 | 0.63 | R21 Batt, 7' depth | 0.035 | 0.56
31 |  | R21 Batt w/TB | WSU | Updated to WSEC 2018 | R21 Batt w/TB, 2' depth | 0.042 | 0.59 | R21 Batt w/TB, 3.5' depth | 0.04 | 0.56 | R21 Batt w/TB, 7' depth | 0.035 | 0.5
32 |  | R21 Batt + R5 ci | 10-1 | Added in WSEC 2018 | R21 Batt + R5 ci, 2' depth | 0.031 | 0.68 | R21 Batt + R5 ci, 3.5' depth | 0.03 | 0.632 | R21 Batt + R5 ci, 7' depth | 0.027 | 0.56
33 |  | R21 Batt + R5 ci w/TB | 10-1 | Added in WSEC 2018 | R21 Batt + R5 ci w/TB, 2' depth | 0.032 | 0.59 | R21 Batt + R5 ci w/TB, 3.5' depth | 0.031 | 0.56 | R21 Batt + R5 ci w/TB, 7' depth | 0.028 | 0.51
34 |  | R21 Batt + R7 ci | 10-1 | Added in WSEC 2018 | R21 Batt + R7 ci, 2' depth | 0.029 | 0.68 | R21 Batt + R7 ci, 3.5' depth | 0.027 | 0.63 | R21 Batt + R7 ci, 7' depth | 0.025 | 0.57
35 |  | R21 Batt + R7 ci w/TB | 10-1 | Added in WSEC 2018 | R21 Batt + R7 ci w/TB, 2' depth | 0.03 | 0.59 | R21 Batt + R7 ci w/TB, 3.5' depth | 0.029 | 0.56 | R21 Batt + R7 ci w/TB, 7' depth | 0.026 | 0.57
36 |  | R21 Batt + R5 ci R10 Fully Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R21 Batt + R5 ci R10 Fully Underslab, 2' depth | 0.031 | 0.35 | R21 Batt + R5 ci R10 Fully Underslab, 3.5' depth | 0.032 | 0.333 | R21 Batt + R5 ci R10 Fully Underslab, 7' depth | 0.029 | 0.307
37 |  | R25 Batt w/TB | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R25 Batt w/TB, 2' depth | 0.038 | 0.593 | R25 Batt w/TB, 3.5' depth | 0.036 | 0.557 | R25 Batt w/TB, 7' depth | 0.032 | 0.505
38 |  | R25 Batt w/TB, R10 Full Underslab | Baylon & Kennedy, https://web.ornl.gov/sci/buildings/conf-archive/2007%20B10%20papers/092_Baylon.pdf | Added 2020 from reference | R25 Batt w/TB, R10 Full Underslab, 2' depth | 0.04 | 0.35 | R25 Batt w/TB, R10 Full Underslab, 3.5' depth | 0.038 | 0.331 | R25 Batt w/TB, R10 Full Underslab, 7' depth | 0.034 | 0.304
|  | == Custom Entries per WSEC R402.1.5 U-factor Reference and Calculations ======== |  |  |  | Wall U | Slab F
110 |  | Test slab | Custom |  |  | 0.05 | 0.5
111 |  |  | Custom |  |  | 0 | 0
112 |  |  | Custom |  |  | 0 | 0
113 |  |  | Custom |  |  | 0 | 0
114 |  |  | Custom |  |  | 0 | 0
115 |  |  | Custom |  |  | 0 | 0
116 |  |  | Custom |  |  | 0 | 0
117 |  |  | Custom |  |  | 0 | 0
======================
Editing Instructions:
Only white areas on the sheet can be edited. Do not delete rows, columns or cells. This will disrupt the indexing reference to the companion worksheet.
Enter component description, and calculated U-factor. Submit the detailed calculations as part of the application for your building permit.
Where proposed construction assemblies are not represented in Appendix A tables, values shall be calculated in accordance with Chapters 21-29 in Standard RS-1 listed in Chapter 5, (ASHRAE Handbook of Fundamentals) using the framing factors listed in Appendix A where applicable.
For envelope assemblies containing metal framing, the U-factor shall be determined by one of the following methods:
1. Results of laboratory or field measurements.
2. Standard RS-25, listed in Chapter 5, where the metal framing is bonded on one or both sides to a metal skin or covering.
3. The zone method as provided in Chapter 24 of Standard RS-1, listed in Chapter 5.
4. Results of parallel path correction factors for effective framing/cavity R-values as provided in TABLE A103.3.6.1(1) : Effective R-Values for Metal Framing and Cavity Only for metal stud walls and roof/ceilings.
Return to Input
Note on C5: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.
Note on C135: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.
Note on F135: On each data tab we have created a “Most Frequently Used” section at the top, which appears on drop down menus and includes the most commonly selected items. Most of the items in this top section are intentionally duplicates of items from the more extensive list below.